{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["废气排放"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气排放","index":0,"n_rows":45,"n_cols":10,"rows_kept":45,"merged":[[0,0,0,9],[2,0,21,0],[22,0,44,0]],"flags":["formulas_cached_only"]}
["2025年第1季度北控环境再生能源（张家港）有限公司监督监测数据"]
["企业名称","执行标准名称","监测点","监测项目","监测日期","实测浓度","折算浓度","上限","单位","是否超标"]
["北控环境再生能源（张家港）有限公司","生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","汞及其化合物","2025-01-07","<0.0056","<0.0056","0.05","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","镉、铊及其化合物（以Cd +Tl计）","2025-01-07","0.000009","0.000006","0.1","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","二噁英类","2025-01-07","0.0023","0.0023","0.1","ng-TEQ/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","锑，砷，铅，铬，钴，铜，锰，镍及其化合物（以Sb+As+Pb+Cr+Co+Cu+Mn+Ni计）","2025-01-07","0.0171","0.0117","1.0","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","一氧化碳","2025-01-07","27","19","100","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","二氧化硫","2025-01-07","<3","<3","100","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","氯化氢","2025-01-07","0.58","0.40","60","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","颗粒物","2025-01-07","<1","<1","30","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","氮氧化物","2025-01-07","127","88","300","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","1#焚烧炉排气筒(FQ -024400057)","焚烧炉渣热灼减率","2025-01-07","2.4","2.4","5","%","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","二噁英类","2025-01-06","0.0038","0.0038","0.1","ng-TEQ/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","焚烧炉渣热灼减率","2025-01-06","2.0","2.0","5","%","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","锑，砷，铅，铬，钴，铜，锰，镍及其化合物（以Sb+As+Pb+Cr+Co+Cu+Mn+Ni计）","2025-01-06","0.0781","0.0559","1.0","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","镉、铊及其化合物（以Cd +Tl计）","2025-01-06","<0.000008","<0.000008","0.1","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","氯化氢","2025-01-06","0.97","0.69","60","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","一氧化碳","2025-01-06","23","16","100","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","颗粒物","2025-01-06","<1","<1","30","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","二氧化硫","2025-01-06","<3","<3","100","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","氮氧化物","2025-01-06","100","71","300","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","3#焚烧炉排气筒(FQ -024400057)","汞及其化合物","2025-01-06","<0.0056","<0.0056","0.05","mg/m3","否"]
["北控环境再生能源（张家港）有限公司","生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","锑，砷，铅，铬，钴，铜，锰，镍及其化合物（以Sb+As+Pb+Cr+Co+Cu+Mn+Ni计）","2025-01-06","0.0471","0.0320","1.0","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","二噁英类","2025-01-06","0.012","0.012","0.1","ng-TEQ/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","一氧化碳","2025-01-06","21","14","100","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","颗粒物","2025-01-06","<1","<1","30","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","氯化氢","2025-01-06","0.50","0.34","60","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","二氧化硫","2025-01-06","<3","<3","100","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","氮氧化物","2025-01-06","108","73","300","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","汞及其化合物","2025-01-06","<0.0056","<0.0056","0.05","mg/m3","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","焚烧炉渣热灼减率","2025-01-06","2.3","2.3","5","%","否"]
[null,"生活垃圾焚烧污染控制标准(GB18485-2014)","2#焚烧炉排气筒(1)","镉、铊及其化合物（以Cd +Tl计）","2025-01-06","<0.000008","<0.000008","0.1","mg/m3","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","铜","2025-01-06","<0.01","<0.01","40","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","钡","2025-01-06","1.20","1.20","25","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","镍 ","2025-01-06","<0.02","<0.02","0.5","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","砷","2025-01-06","0.00414","0.00414","0.3","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","锌","2025-01-06","0.04","0.04","100","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","总铬","2025-01-06","0.08","0.08","4.5","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","硒","2025-01-06","0.0760","0.0760","0.1","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","铍","2025-01-06","<0.004","<0.004","0.02","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","汞","2025-01-06","0.00192","0.00192","0.05","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","铅","2025-01-06","<0.03","<0.03","0.25","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","镉","2025-01-06","<0.01","<0.01","0.15","mg/L","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","含水率（%）","2025-01-06","23.6","23.6","30","%","否"]
[null,"生活垃圾填埋场污染控制标准(GB16889-2008)","飞灰车间","六价铬","2025-01-06","<0.004","<0.004","1.5","mg/L","否"]